Paradise Taveuni

ESP32 Dashboard API — Data Schema Reference

Version 1.0  |  March 2026  |  For Developer Use

# 1. Overview

The Paradise Taveuni ESP32 gateway reads data from on-site solar and energy monitoring devices over Modbus RS-485, then packages it into a JSON payload and posts it to AWS every 60 seconds.

This document defines the exact JSON schema your dashboard must consume. During the testing phase a dummy ESP32 device (gateway_id: ESP32-DUMMY-001) sends static representative data so you can build and test the dashboard before the live site is online.

# 2. API Endpoint

| Property | Value |
| --- | --- |
| Method | POST |
| URL | https://0nriesk3fl.execute-api.ap-southeast-2.amazonaws.com/dev-esp32/esp32datahandler |
| Auth Header | x-api-key: f2zBDNoc3saOza8lOgnMq7nFC52HjiUb1q0uIyci |
| Content-Type | application/json |
| Interval | Every 60 seconds |
| Database | AWS DynamoDB (ap-southeast-2) |

# 3. Top-Level Payload Structure

Each POST body is a single JSON object with the following top-level fields:

| Field | Type | Description | Example Value |
| --- | --- | --- | --- |
| client_name | String | Human-readable site owner name | Paradise Resort |
| client_email | String | Contact email for the site owner | example@paradise.com |
| client_ID | String | Unique client identifier | 001 |
| site_id | String | Unique site identifier | 1 |
| gateway_id | String | Unique ESP32 device identifier | ESP32-DUMMY-001 |
| fw | String | Firmware version string | paradise-esp32-dummy-1.0 |
| ts_epoch_ms | Number | UTC timestamp in milliseconds since Unix epoch | 1711411200000 |
| meters | Array | Array of energy meter objects (see Meters) | [ ... ] |
| inverters | Array | Array of inverter objects (see Inverters) | [ ... ] |

# 4. Meters Array

The meters array contains one object per energy meter. Each object always includes slave_id, p_total_w, and kwh_total. Dual-tariff meters additionally include kwh_t1 and kwh_t2.

| Field | Type | Description | Example Value |
| --- | --- | --- | --- |
| slave_id | Number | Modbus slave address | 11 |
| p_total_w | Number | Total active power in Watts | 4200.0 |
| kwh_total | Number | Cumulative energy — all tariffs (kWh) | 1800.0 |
| kwh_t1 | Number | Cumulative energy — Tariff 1 (kWh). Dual-tariff only | 8000.0 |
| kwh_t2 | Number | Cumulative energy — Tariff 2 (kWh). Dual-tariff only | 1500.0 |

# 5. Inverters Array

The inverters array contains one object per Deye inverter. Each inverter has 4 MPPT inputs, so mppt_kw will always be an array of 4 numbers for this site.

| Field | Type | Description | Example Value |
| --- | --- | --- | --- |
| slave_id | Number | Modbus slave address | 1 |
| status | String | Operational state: running ¦ fault ¦ standby ¦ off | running |
| p_total_w | Number | Total PV generation power in Watts | 38000.0 |
| mppt_kw | Array | Per-MPPT string output in Watts. Array length = MPPT count | [9800, 9500, 9200, 9500] |
| bat_soc | Number | Battery state of charge in percent (0–100) | 72 |

# 6. Device Map — Paradise Taveuni

The following devices are installed at this site. Slave IDs are fixed and will remain consistent between dummy and live data.

| Slave ID | Device Type | Tariff Mode | Notes |
| --- | --- | --- | --- |
| 11 | Energy Meter | Single-tariff | Grid/building supply meter |
| 12 | Energy Meter | Dual-tariff | Main load — large building |
| 13 | Energy Meter | Dual-tariff | Main load — secondary building |
| 14 | Energy Meter | Single-tariff | Sub-load meter |
| 15 | Energy Meter | Single-tariff | Sub-load meter |
| 1 | Deye 50kW Inverter | — | Solar inverter #1, 4 MPPT strings |
| 2 | Deye 50kW Inverter | — | Solar inverter #2, 4 MPPT strings |
| 3 | Deye 50kW Inverter | — | Solar inverter #3, 4 MPPT strings |

# 7. Implementation Notes

## Dummy vs Live Data

During development, all payloads come from gateway_id: ESP32-DUMMY-001 with static values. When the live ESP32 is commissioned, the gateway_id will change (e.g. ESP32-PARADISE-001) and values will reflect real site readings. The JSON structure will be identical.

## Timestamp

ts_epoch_ms is a Unix timestamp in milliseconds (UTC). To convert to a local datetime in JavaScript:

new Date(ts_epoch_ms).toISOString()   // UTC ISO string

new Date(ts_epoch_ms).toLocaleString() // local time

## Power vs Energy

p_total_w is instantaneous power in Watts — use this for real-time display (e.g. gauges, live charts). kwh_total / kwh_t1 / kwh_t2 are cumulative energy counters in kWh — use these for energy reports and trend charts. These counters only increase over time (they reset if a meter is replaced).

## MPPT Values

mppt_kw values are labelled in watts despite the field name. Each element corresponds to one MPPT string input on the inverter. For this site, all inverters have 4 inputs, so the array will always have 4 elements.

## SSL / TLS

The ESP32 connects to AWS using WiFiClientSecure with certificate verification disabled (setInsecure). The HTTPS connection is still encrypted in transit. The dashboard should connect to AWS using standard HTTPS.

# 8. Example Payload

The following is a complete example payload as sent by the dummy ESP32:

{

"client_name":  "Paradise Resort",

"client_email": "example@paradise.com",

"client_ID":    "001",

"site_id":      "1",

"gateway_id":   "ESP32-DUMMY-001",

"fw":           "paradise-esp32-dummy-1.0",

"ts_epoch_ms":  1711411200000,

"meters": [

{ "slave_id": 11, "p_total_w": 4200.0, "kwh_total": 1800.0 },

{ "slave_id": 12, "p_total_w": 15000.0, "kwh_total": 9500.0, "kwh_t1": 8000.0, "kwh_t2": 1500.0 },

{ "slave_id": 13, "p_total_w": 12000.0, "kwh_total": 7200.0, "kwh_t1": 6000.0, "kwh_t2": 1200.0 },

{ "slave_id": 14, "p_total_w": 3800.0, "kwh_total": 2100.0 },

{ "slave_id": 15, "p_total_w": 2500.0, "kwh_total": 1400.0 }

],

"inverters": [

{ "slave_id": 1, "status": "running", "p_total_w": 38000.0,

"mppt_kw": [9800.0, 9500.0, 9200.0, 9500.0], "bat_soc": 72 },

{ "slave_id": 2, "status": "running", "p_total_w": 36000.0,

"mppt_kw": [9200.0, 9000.0, 8800.0, 9000.0], "bat_soc": 68 },

{ "slave_id": 3, "status": "running", "p_total_w": 35000.0,

"mppt_kw": [8800.0, 8800.0, 8700.0, 8700.0], "bat_soc": 65 }

]

}